## LINER DECK & AQUAPANEL
Project Name: | [8 empty] | Name | Company | Role | Date of Review | Contact Details |  | Inspection & Test Key
Project Code: | [7 empty] | ITP Prepared By: | [6 empty] | I | Inspection
ITP Title: | [7 empty] | GT Review By: | [6 empty] | T | Test
ITP Ref No: | [7 empty] | GT Input/Review By: | [6 empty] | Monitoring Requirements Key
Revision Ref | Reason for Revision |  |  | Date |  |  |  | GT Input/Review By: | [6 empty] | H | HOLD Point
0 | First Issue |  |  | 2024-09-16 |  |  |  | GT Input/Review By: | [6 empty] | W(%) | Witness (%)
[8 empty] | Input/Review by | [6 empty] | SFA | Submits for Approval
[8 empty] | Input/Review by | [6 empty] | A | Approves
[8 empty] | ITP Authorised for use by: | [6 empty] | R | Receives Record
ITP Signed off & all records complete
ITP Signed off & all records complete
ITP Input Information
[8 empty] | Source / Document |  |  | Reference (if applicable) |  | Revision
Stage | Ref | Activity / Description | Inspection or Test (use a separate line for each Inspection or Test) |  |  |  | Requirement |  | Verification (method of checking) | Frequency (of check) | Locations (of checks) | Records (detail the Evidence that will prove the requirement has been met) | Who is responsible (for closing out the requirement) | Monitoring Requirements
|  |  | at source | at delivery | in progress | final | Where from (document & clause) | What is the requirement (acceptance criteria) | [5 empty] | S/C | PC | Designer | Client's Rep | Other
Pre-Construction | 1
1.1
1.2
1.3
1.4
1.5
Material Conformity (including CE & Kite Marking) | 2.0
2.1
2.2
2.3
2.4
2.5
Off-site manufacture | 3.0
3.1
3.2
3.3
3.4
3.5
Delivery | 4.0
4.1
4.2
4.3
4.4
4.5
Pre Start | 5.0
5.1
5.2
5.3
5.4
5.5
In Progress | 6.0
6.1
6.2
6.3
6.4
6.5
6.6
6.7
6.8
6.9
6.10
Completion Checks | 7.0
7.1
7.2
7.3
7.4
7.5
Testing & Commissioning | 8.0
8.1
8.2
8.3
8.4
8.5
Handover & Close out | 9
9.1
9.2
9.3
9.4
9.5

## FELT TO METAL DECK AREA
Project Name: | Paisley Grammar | [7 empty] | Name | Company | Role | Date of Review | Contact Details |  | Inspection & Test Key
Project Code: | [7 empty] | ITP Prepared By: | Graeme Ritchie | Q9 | Contracts Mgr |  |  |  | I | Inspection
ITP Title: | [7 empty] | GT Review By: |  | GT | WPT Specialist |  |  |  | T | Test
ITP Ref No: | [7 empty] | GT Input/Review By: |  | GT | DM Lead |  |  |  | Monitoring Requirements Key
Revision Ref | Reason for Revision |  |  | Date |  |  |  | GT Input/Review By: |  | GT | Project Lead |  |  |  | H | HOLD Point
0 | First Issue |  |  | 2024-09-16 |  |  |  | GT Input/Review By: |  | GT | Technical |  |  |  | W(%) | Witness (%)
1 | Felt Added |  |  | 2024-10-28 |  |  |  | Input/Review by |  |  | Consultant |  |  |  | SFA | Submits for Approval
[8 empty] | Input/Review by |  |  | Client/TA |  |  |  | A | Approves
[8 empty] | ITP Authorised for use by: |  | GT | WPT Specialist |  |  |  | R | Receives Record
[8 empty] | ITP Signed off & all records complete |  | GT | WPT Specialist
[8 empty] | ITP Signed off & all records complete |  | WP Contractor
ITP Input Information
[8 empty] | Source / Document |  |  | Reference (if applicable) |  | Revision
Stage | Ref | Activity / Description | Inspection or Test (use a separate line for each Inspection or Test) |  |  |  | Requirement |  | Verification (method of checking) | Frequency (of check) | Locations (of checks) | Records (detail the Evidence that will prove the requirement has been met) | Who is responsible (for closing out the requirement) | Monitoring Requirements
|  |  | at source | at delivery | in progress | final | Where from (document & clause) | What is the requirement (acceptance criteria) | [5 empty] | S/C | PC | Designer | Client's Rep | Other
Pre-Construction | 1
1.1
1.2
1.3
1.4
1.5
Material Conformity (including CE & Kite Marking) | 2.0
2.1
2.2
2.3
2.4
2.5
Off-site manufacture | 3.0
3.1
3.2
3.3
3.4
3.5
Delivery | 4.0 | Delivery of Materials |  | I |  |  | N/A | All materials comply with those described on the Material Approval Request forms. | All materials to be inspected prior to or immediately after un-loading to ensure: 1) The material described on the Delivery Ticket is that described on the Material Approval Request (MAR). 2) The material being delivered complies with that described on the Delivery Ticket (type and quantity) 3) The material being delivered is not damaged. | Every delivery | At point of delivery / un-loading | Signed Delivery Ticket - with written confirmation that the delivery complies with the MAR. | Q9 Site Management
4.1
4.2
4.3
4.4
4.5
Pre Start | 5.0 | Aquapanel Completion |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | Aquapael completed & Signed off | Check Drawings / Quality Inspection Sheet | Each Zone | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | N/A | R | N/A
5.1
5.2
5.3
5.4
5.5
In Progress | 6.0 | Primer |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | BAUDER ACTIVATOR-PRIMER (CANISTER), APR01-BLACK, APPLIED TO THE ROOF SUBSTRATE AND ALL UPSTANDS AND SKIRTINGS (100% COVERAGE TO SUBSTRATE. | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.1 | AVCL |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | BAUDERTEC KSD FBS, 2.5 MM THICK, ELASTOMERIC BITUMEN SELF-ADHESIVE AIR AND VAPOUR CONTROL LAYER MICA FINISH. (Min 100mm SIDE & END LAPS) | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
| 6.2 | Insulation |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | 360mm THK BAUDER PIR FA-TE INSULATION BOARD (200+160mm), ADHERED TO AQUAPANEL USING BAUDER PU INSULATION ADHESIVE applied in 10-20mm BEADS. 3 RUNS OF ADHESIVE TO PERIMETER ZONES 2 RUNS OF ADHESIVE TO FIELD AREA. | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.3 | Insulation to Insulation Adhesive |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | BAUDER PIR FA-TE INSULATION BOARDS BONDED TOGETHER USING BAUDER ACTIVATOR PRIMER (CANISTER) APR01 BLACK. FULL SPRAY COVERAGE TO BOTH SURFACES IN PERIMETER ZONES FULLY SPRAY COVERAGE TO BOTTOM BOARD = 100% COVERAGE & 2 No. CONTINUOUS STRIPS TO TOP BOARD = 50% COVERAGE | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
| 6.4 | Underlay |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | PRIMER: BAUDER ACTIVATOR-PRIMER (CANISTER), APR01-BLACK, APPLIED TO THE UPPER SURFACE OF THE BAUDER INSULATION (100% COVERAGE) BAUDER TEC KSA DUO, 3 MM THICK, 200G/M² GLASS-FIBRE REINFORCED, ELASTOMERIC SELF-ADHESIVE BITUMEN UNDERLAYER. COLD APPLIED AND FULLY BONDED BY REMOVING THE PEEL OFF RELEASE FILM. THE SIDE LAPS ARE TO BE 100MM AND MUST BE LAID RED OVER BLUE, AND HEAT SEALED/TORCHED. HEAD LAPS TO BE 100MM AND STAGGERED. (ALL LAPS TO EXTRUDE A CONTINUOUS BEAD OF BITUMEN) | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
| 6.5 | Cap Sheet |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | BAUDER K5K, 5.2 MM THICK, TENSILE STRENGTH 1000N/50MM, 250G/M² POLYESTER REINFORCED, ELASTOMERIC BITUMEN TORCH APPLIED CAPPING SHEET, CHARCOAL GREY FINISH (80mm SIDE LAPS, 100mm END LAPS) HEAD LAPS TO BE 100MM AND STAGGERED. (ALL LAPS TO EXTRUDE A CONTINUOUS BEAD OF BITUMEN) | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.6 | Upstands & Detail Work |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | As Above | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
Completion Checks | 7.0
7.1
7.2
7.3
7.4
7.5
Testing & Commissioning | 8.0
8.1
8.2
8.3
8.4
8.5
Handover & Close out | 9
9.1
9.2
9.3
9.4
9.5

## FELT TO CONCRETE AREA
Project Name: | Paisley Grammar | [7 empty] | Name | Company | Role | Date of Review | Contact Details |  | Inspection & Test Key
Project Code: | [7 empty] | ITP Prepared By: | Graeme Ritchie | Q9 | Contracts Mgr |  |  |  | I | Inspection
ITP Title: | [7 empty] | GT Review By: |  | GT | WPT Specialist |  |  |  | T | Test
ITP Ref No: | [7 empty] | GT Input/Review By: |  | GT | DM Lead |  |  |  | Monitoring Requirements Key
Revision Ref | Reason for Revision |  |  | Date |  |  |  | GT Input/Review By: |  | GT | Project Lead |  |  |  | H | HOLD Point
0 | First Issue |  |  | 2024-09-16 |  |  |  | GT Input/Review By: |  | GT | Technical |  |  |  | W(%) | Witness (%)
1 | Felt Added |  |  | 2024-10-28 |  |  |  | Input/Review by |  |  | Consultant |  |  |  | SFA | Submits for Approval
[8 empty] | Input/Review by |  |  | Client/TA |  |  |  | A | Approves
[8 empty] | ITP Authorised for use by: |  | GT | WPT Specialist |  |  |  | R | Receives Record
[8 empty] | ITP Signed off & all records complete |  | GT | WPT Specialist
[8 empty] | ITP Signed off & all records complete |  | WP Contractor
ITP Input Information
[8 empty] | Source / Document |  |  | Reference (if applicable) |  | Revision
Stage | Ref | Activity / Description | Inspection or Test (use a separate line for each Inspection or Test) |  |  |  | Requirement |  | Verification (method of checking) | Frequency (of check) | Locations (of checks) | Records (detail the Evidence that will prove the requirement has been met) | Who is responsible (for closing out the requirement) | Monitoring Requirements
|  |  | at source | at delivery | in progress | final | Where from (document & clause) | What is the requirement (acceptance criteria) | [5 empty] | S/C | PC | Designer | Client's Rep | Other
Pre-Construction | 1
1.1
1.2
1.3
1.4
1.5
Material Conformity (including CE & Kite Marking) | 2.0
2.1
2.2
2.3
2.4
2.5
Off-site manufacture | 3.0
3.1
3.2
3.3
3.4
3.5
Delivery | 4.0 | Delivery of Materials |  | I |  |  | N/A | All materials comply with those described on the Material Approval Request forms. | All materials to be inspected prior to or immediately after un-loading to ensure: 1) The material described on the Delivery Ticket is that described on the Material Approval Request (MAR). 2) The material being delivered complies with that described on the Delivery Ticket (type and quantity) 3) The material being delivered is not damaged. | Every delivery | At point of delivery / un-loading | Signed Delivery Ticket - with written confirmation that the delivery complies with the MAR. | Q9 Site Management
4.1
4.2
4.3
4.4
4.5
Pre Start | 5.0 | Aquapanel Completion |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | Aquapael completed & Signed off | Check Drawings / Quality Inspection Sheet | Each Zone | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | N/A | R | N/A
| 5.1 | Peel Test Carried out |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | Suitable Adhesion of VCL to Concrete | Check Drawings / Quality Inspection Sheet | Each Zone | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | N/A | R | N/A
5.2
5.3
5.4
5.5
In Progress | 6.0 | Primer |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | BAUDER QUICK DRY PRIMER APPLIED TO THE ROOF SUBSTRATE AND ALL UPSTANDS AND SKIRTINGS (100% COVERAGE TO SUBSTRATE. | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.1 | AVCL |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | BAUDERTEC SUPER AL-E 3.5MM THICK, ELASTOMERIC BITUMEN SELF-ADHESIVE AIR AND VAPOUR CONTROL LAYER (Min 100mm SIDE & END LAPS) | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
| 6.2 | Insulation |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | 360mm THK BAUDER PIR FA-TE INSULATION BOARD (200+160mm), ADHERED TO AQUAPANEL USING BAUDER PU INSULATION ADHESIVE applied in 10-20mm BEADS. 3 RUNS OF ADHESIVE TO PERIMETER ZONES 2 RUNS OF ADHESIVE TO FIELD AREA. | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.3 | Insulation to Insulation Adhesive |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | BAUDER PIR FA-TE INSULATION BOARDS BONDED TOGETHER USING BAUDER ACTIVATOR PRIMER (CANISTER) APR01 BLACK. FULL SPRAY COVERAGE TO BOTH SURFACES IN PERIMETER ZONES FULLY SPRAY COVERAGE TO BOTTOM BOARD = 100% COVERAGE & 2 No. CONTINUOUS STRIPS TO TOP BOARD = 50% COVERAGE | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
| 6.4 | Underlay |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | PRIMER: BAUDER ACTIVATOR-PRIMER (CANISTER), APR01-BLACK, APPLIED TO THE UPPER SURFACE OF THE BAUDER INSULATION (100% COVERAGE) BAUDER TEC KSA DUO, 3 MM THICK, 200G/M² GLASS-FIBRE REINFORCED, ELASTOMERIC SELF-ADHESIVE BITUMEN UNDERLAYER. COLD APPLIED AND FULLY BONDED BY REMOVING THE PEEL OFF RELEASE FILM. THE SIDE LAPS ARE TO BE 100MM AND MUST BE LAID RED OVER BLUE, AND HEAT SEALED/TORCHED. HEAD LAPS TO BE 100MM AND STAGGERED. (ALL LAPS TO EXTRUDE A CONTINUOUS BEAD OF BITUMEN) | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
| 6.5 | Cap Sheet |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | BAUDER K5K, 5.2 MM THICK, TENSILE STRENGTH 1000N/50MM, 250G/M² POLYESTER REINFORCED, ELASTOMERIC BITUMEN TORCH APPLIED CAPPING SHEET, CHARCOAL GREY FINISH (80mm SIDE LAPS, 100mm END LAPS) HEAD LAPS TO BE 100MM AND STAGGERED. (ALL LAPS TO EXTRUDE A CONTINUOUS BEAD OF BITUMEN) | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.6 | Upstands & Detail Work |  |  | I |  | 21012-RYD-XX-XX-SP-A-0005_Roofs_(A5) Construction_C2 | As Above | Check Drawings / Quality Inspection Sheet | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
Completion Checks | 7.0
7.1
7.2
7.3
7.4
7.5
Testing & Commissioning | 8.0
8.1
8.2
8.3
8.4
8.5
Handover & Close out | 9
9.1
9.2
9.3
9.4
9.5

## K-ROCK COMPOSITE PANELS
Project Name: | Paisley Grammar | [7 empty] | Name | Company | Role | Date of Review | Contact Details |  | Inspection & Test Key
Project Code: | [7 empty] | ITP Prepared By: | Graeme Ritchie | Q9 | Contracts Mgr |  |  |  | I | Inspection
ITP Title: | [7 empty] | GT Review By: |  | GT | WPT Specialist |  |  |  | T | Test
ITP Ref No: | [7 empty] | GT Input/Review By: |  | GT | DM Lead |  |  |  | Monitoring Requirements Key
Revision Ref | Reason for Revision |  |  | Date |  |  |  | GT Input/Review By: |  | GT | Project Lead |  |  |  | H | HOLD Point
0 | First Issue |  |  | 2024-09-16 |  |  |  | GT Input/Review By: |  | GT | Technical |  |  |  | W(%) | Witness (%)
1 | Felt Added |  |  | 2024-10-28 |  |  |  | Input/Review by |  |  | Consultant |  |  |  | SFA | Submits for Approval
2 | K-ROCK Added |  |  | 2025-01-24 |  |  |  | Input/Review by |  |  | Client/TA |  |  |  | A | Approves
3 | Rainscreen Added |  |  | 2025-03-12 |  |  |  | ITP Authorised for use by: |  | GT | WPT Specialist |  |  |  | R | Receives Record
[8 empty] | ITP Signed off & all records complete |  | GT | WPT Specialist
[8 empty] | ITP Signed off & all records complete |  | WP Contractor
ITP Input Information
[8 empty] | Source / Document |  |  | Reference (if applicable) |  | Revision
Stage | Ref | Activity / Description | Inspection or Test (use a separate line for each Inspection or Test) |  |  |  | Requirement |  | Verification (method of checking) | Frequency (of check) | Locations (of checks) | Records (detail the Evidence that will prove the requirement has been met) | Who is responsible (for closing out the requirement) | Monitoring Requirements
|  |  | at source | at delivery | in progress | final | Where from (document & clause) | What is the requirement (acceptance criteria) | [5 empty] | S/C | PC | Designer | Client's Rep | Other
Pre-Construction | 1
1.1
1.2
1.3
1.4
1.5
Material Conformity (including CE & Kite Marking) | 2.0
2.1
2.2
2.3
2.4
2.5
Off-site manufacture | 3.0
3.1
3.2
3.3
3.4
3.5
Delivery | 4.0 | Delivery of Materials |  | I |  |  | N/A | All materials comply with those described on the Material Approval Request forms. | All materials to be inspected prior to or immediately after un-loading to ensure: 1) The material described on the Delivery Ticket is that described on the Material Approval Request (MAR). 2) The material being delivered complies with that described on the Delivery Ticket (type and quantity) 3) The material being delivered is not damaged. | Every delivery | At point of delivery / un-loading | Signed Delivery Ticket - with written confirmation that the delivery complies with the MAR. | Q9 Site Management
4.1
4.2
4.3
4.4
4.5
Pre Start | 5.0 | Steel / SFS lined & levelled to accept panels |  |  | I |  |  |  | Handover Sheet | Each Zone | Each Zone | Photographs / Joint inspection | Steel Contractor | I | I | N/A | R | N/A
| 5.1 | Alignment / Level of steel / SFS acceptable |  |  | I |  |  |  | Handover Sheet | Each Zone | Each Zone | Photographs / Joint inspection | SFS Contractor | I | I | N/A | R | N/A
| 5.2 | Gas Membrane complete at Base |  |  | I |  |  |  | Handover Sheet | Each Zone | Each Zone | Photographs / Joint inspection | Ground Works Contractor | I | I | N/A | R | N/A
5.3
5.4
5.5
FIRST FIX FLASHINGS & SEALS – BASE DETAIL
In Progress | 6.0 | VISQUEEN DETAILING STRIP |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | VISQUEEN PRO DETAILING STRIP SEALED TO REAR OF LEDGER & DPM | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.1 | 2mm GALVE LEDGER ANGLE |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | RIVETED WITH PG-CALA2-4.8x10 RIVET FIXED INTO EVERY SFS STUD. JOINTS TO BE TAPED WITH 50X1 SWRP TAPE. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.2 | RWA45 INSULATION INFILL |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | PACKED INTO GAP BETWEEN LEDGER ANGLE & DPM | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.3 | ADDITIONAL VISQUEEN DETAILING STRIP |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | VISQUEEN PRO DETAILING STRIP SEALED TO TOP OF LEDGER & DPM | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.4 | 20 x 9 SVG15PL FOAM TAPE |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | APPLIED CONTINIOUSLY TO VERTICAL FACE OF LEDGE ANGLE. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.5 | GUN GRADE MASTIC |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | BEAD APPLIED CONTINIOUSLY TO VERTICAL FACE OF LEDGE ANGLE ABOVE SVG15 FOAM TAPE | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
FIRST FIX FLASHINGS & SEALS – PANEL JOINTS
| 6.6 | VERTICAL PANEL JOINTS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | VJ2 BUBBLE GASKET APPLIED CONTINIOUSLY TO SFS STUDS AT VERTICAL PANEL JOINT LOCATIONS 20x9 SGV15Pl FOAM TAPE TO REAR OF PANEL APPLIED PRIOR TO PANEL INSTALL | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
FIRST FIX FLASHINGS & SEALS – DEFLECTION JOINT
| 6.7 | 2mm GALVE FLAT PLATES |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | FIXED TO SFS ABOVE & BELOW DEFLECTION JOINT. RIVERTED SFS VERTICAL STUDS WITH 2 No. PG-C-ALA2-4.8x10 PER STUD | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.8 | EPDM |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | OBEX 0500 FR BONDED TO BOTH GALV FLAT PLATES. BAGGED TO ALLOW DEFLECTION WITHOUT DAMAGE TO THE EPDM MEMBRANE | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.9 | 2mm LEDGER ANGLE |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | GALV LEDGER BONDED TO OBEX 0500 FR MEMBRANE WITH GUN GRADE MASTIC & RIVETED TO GALV FLAT PLATE @ 300mm CTR's. JOINTS IN LEDGER ANGLE TAPED WITH 50X1 SWRP TAPE | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
FIRST FIX FLASHINGS & SEALS – HEAD DETAIL
| 6.1 | BAUDER VCL |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | BAUDERTEC KSD MICA VCL CONTINUOUSLY LAID ACROSS COPING & SEALED TO SFS HEAD TRACK PRIOR TO PANEL INSTALL. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.11 | 20X9 SGV15PL FOAM TAPE |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | APPLIED BETWEEN VCL & BACK OF PANEL PRIOR TO PANEL INSTALL | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.12 | GUN GRADE MASTIC |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | BEAD APPLIED CONTINIOUSLY TO VCL ABOVE SVG15 FOAM TAPE | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
FIRST FIX FLASHINGS & SEALS – INTERNAL & EXTERNAL CORNERS
| 6.13 | 2.0mm GALVE ANGLE |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | JOINTS TAPED WITH SRWP 50X1 TAPE. RIVETED TO SFS STUD @500mm CTRs WITH PG-C-ALA2-4.8x10 | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.14 | PRIMARY SEALS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | GUN APPLIED BUTYL GUN MASTIC BETWEEN PANEL & GALV. 20 x 9 SGV15 FOAM TAPE BETWEEN PANEL & GALVE. APPLIED PRIOR TO PANEL INSTALL | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
FIRST FIX FLASHINGS & SEALS – WINDOW HEAD, JAMB & BASE
| 6.15 | 1.5mm LEDGER ANGLE TO WINDOW HEAD |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | LEDGER RIVETED TO EACH SFS STUD WITH PG-C-ALA2-4.8x10. GUN APPLIED MASTIC BETWEEN LEDGE ANGLE & SFS BASE TRACK. JOINTS TAPED WITH SRWP 50X1 TAPE. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.16 | PRIMARY SEALS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | GUN APPLIED BUTYL GUN MASTIC BETWEEN PANEL & GALV. 20 x 9 SGV15 FOAM TAPE BETWEEN PANEL & LEDGER. APPLIED PRIOR TO PANEL INSTALL. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.17 | 1.5mm GLAVE ANGLE TO WINDOW / DOOR JAMB & CILL |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | RIVETED TO SFS STUD WITH PG-C-ALA2-4.8x10 @ 450CTR's | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.18 | PRIMARY SEALS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | GUN APPLIED BUTYL GUN MASTIC BETWEEN PANEL & GALV. 20 x 9 SGV15 FOAM TAPE BETWEEN PANEL & GALVE ANGLE. APPLIED PRIOR TO PANEL INSTALL. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.19 | OBEX CORTEX 0901 FR |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | PRE FORMED EPDM CORNER INSTALLED BETWEEN WINDOW JAMB GALVE & LEDGE TO PROVIDE CONTINUATION OF AIR SEAL | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
K-ROCK COMPOSITE PANELS
| 6.2 | PANEL SPEC |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | KINGSPAN K-ROCK KARRIER PANELS – 300MM CORE THICKNESS | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.21 | PANEL FIXINGS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | FIXED TO SFS STUDS WITH SXC5-6.3X345 C/W EJOT® HTV 82/40 DEEP DIMPLE PLATES | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.22 | FIXING FREQUENCY – CORNER ZONES |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | 3 NO. SXC5-6.3X290 C/W EJOT® HTV 82/40 DEEP DIMPLE @ TYPICAL INTERMEDIATE SFS STUDS 2 NO. SXC5-6.3X290 C/W EJOT® HTV 82/40 DEEP DIMPLE @ ALL PANEL ENDS | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.23 | FIXING FREQUENCY – REMAINING AREAS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | 2 NO. SXC5-6.3X290 C/W EJOT® HTV 82/40 DEEP DIMPLE @ TYPICAL INTERMEDIATE SFS STUDS 2 NO. SXC5-6.3X290 C/W EJOT® HTV 82/40 DEEP DIMPLE @ ALL PANEL ENDS | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
K-ROCK COMPOSITE PANEL SEALS & INSULATION INFILL
| 6.24 | HORIZONTAL JOINTS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | SITE APPLIED BUTYL GUN MASTIC TO INTERNAL JOINT. KINGSPAN FACTORY APPLIED SEAL TO INTERNAL & EXTERNAL JOINT. HORIZONTAL JOINTS ACROSS DEPTH OF PANELS TO BE INFILLED WITH GUN GRADE MASTIC LOCALLY TO CONNECT AIR SEALS. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.25 | VERTICAL JOINTS & INTERNAL & EXTERNAL CORNERS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | INFILLED WITH ROCKWOOL INSULATION INFILLMINIMUM 40kg/m³ DENSITY. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.26 | INTERNAL CORNER SEALS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | 100x1 SWRP10 TAPE TO SEAL INTERNAL CORNER APPLIED CONTINIOUSLY TO FACE OF BOTH PANELS. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | H | R | R
PROCTOR WRAPTITE MEMBRANE UV
| 6.27 | APPLICATION |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | SELF ADHESIVE MEMBRAE APPLIED TO OUTER FACE OF K-ROCK PANELS. TO BE APPLIED IN DRY WEATHER. USE HAND ROLLERS & STIFF BRUSHES TO ENSURE CORRECT ADHEASION TO SUBSTRATE | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.28 | LAPS |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | ALL HORIZONTAL & VERTICAL LAPS TO BE MIN 75MM. INTERNAL & EXTERNAL CORNERS LAPS TO BE MIN 150MM | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.29 | BASE DETAIL |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | TO BE FULLY SEALED TO DPM MEMBRANE. GAP BETWEEN PANEL & DPM TO BE PACKED WITH RWA45 INSULATION PRIOR TO WRAPTITE APPLICATION | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.3 | HEAD DETAIL |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | TO BE TAKEN ACROSS TO OF K-ROCK PANEL & BONDED TO BAUDER KSD MICA VCL. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.31 | APETURES |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | TO BE RETURNED INTO ALL OPENINGS & BONDED TO THE FACE OF SFS STUDS. | Check Drawings / Quality Inspection Sheet - K-ROCK Composite Panels | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
Completion Checks | 7.0
7.1
7.2
7.3
7.4
7.5
Testing & Commissioning | 8.0
8.1
8.2
8.3
8.4
8.5
Handover & Close out | 9
9.1
9.2
9.3
9.4
9.5

## RAINSCREEN
Project Name: | Paisley Grammar | [7 empty] | Name | Company | Role | Date of Review | Contact Details |  | Inspection & Test Key
Project Code: | [7 empty] | ITP Prepared By: | Graeme Ritchie | Q9 | Contracts Mgr |  |  |  | I | Inspection
ITP Title: | [7 empty] | GT Review By: |  | GT | WPT Specialist |  |  |  | T | Test
ITP Ref No: | [7 empty] | GT Input/Review By: |  | GT | DM Lead |  |  |  | Monitoring Requirements Key
Revision Ref | Reason for Revision |  |  | Date |  |  |  | GT Input/Review By: |  | GT | Project Lead |  |  |  | H | HOLD Point
0 | First Issue |  |  | 2024-09-16 |  |  |  | GT Input/Review By: |  | GT | Technical |  |  |  | W(%) | Witness (%)
1 | Felt Added |  |  | 2024-10-28 |  |  |  | Input/Review by |  |  | Consultant |  |  |  | SFA | Submits for Approval
2 | K-ROCK Added |  |  | 2025-01-24 |  |  |  | Input/Review by |  |  | Client/TA |  |  |  | A | Approves
3 | Rainscreen Added |  |  | 2025-03-12 |  |  |  | ITP Authorised for use by: |  | GT | WPT Specialist |  |  |  | R | Receives Record
[8 empty] | ITP Signed off & all records complete |  | GT | WPT Specialist
[8 empty] | ITP Signed off & all records complete |  | WP Contractor
ITP Input Information
[8 empty] | Source / Document |  |  | Reference (if applicable) |  | Revision
Stage | Ref | Activity / Description | Inspection or Test (use a separate line for each Inspection or Test) |  |  |  | Requirement |  | Verification (method of checking) | Frequency (of check) | Locations (of checks) | Records (detail the Evidence that will prove the requirement has been met) | Who is responsible (for closing out the requirement) | Monitoring Requirements
|  |  | at source | at delivery | in progress | final | Where from (document & clause) | What is the requirement (acceptance criteria) | [5 empty] | S/C | PC | Designer | Client's Rep | Other
Pre-Construction | 1
1.1
1.2
1.3
1.4
1.5
Material Conformity (including CE & Kite Marking) | 2.0
2.1
2.2
2.3
2.4
2.5
Off-site manufacture | 3.0
3.1
3.2
3.3
3.4
3.5
Delivery | 4.0 | Delivery of Materials |  | I |  |  | N/A | All materials comply with those described on the Material Approval Request forms. | All materials to be inspected prior to or immediately after un-loading to ensure: 1) The material described on the Delivery Ticket is that described on the Material Approval Request (MAR). 2) The material being delivered complies with that described on the Delivery Ticket (type and quantity) 3) The material being delivered is not damaged. | Every delivery | At point of delivery / un-loading | Signed Delivery Ticket - with written confirmation that the delivery complies with the MAR. | Q9 Site Management
4.1
4.2
4.3
4.4
4.5
Pre Start | 5.0 | K-Roc Composite panels complete |  |  | I |  |  |  | Q9 Quality Checksheet - K-Roc Panels | Each Zone | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | N/A | R | N/A
| 5.1 | Proctor Wraptite complete |  |  | I |  |  |  | Q9 Quality Checksheet - K-Roc Panels | Each Zone | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | N/A | R | N/A
| 5.2 | Glazing & Glazing EPDM’s complete |  |  | I |  |  |  | Handover Sheet | Each Zone | Each Zone | Photographs / Joint inspection | Glazing Contractor | I | I | N/A | R | N/A
5.3
5.4
5.5
FIRST FIX TO PROFILED CLADDING
In Progress | 6.0 | Horizontal Top Hats |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | 3mm THK GALV STEEL. KSSVG25 FOAM TAPE APPPLIED TO LEGS, BETWEEN TOPHAT AND PROCTOR WRAPTITE | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.1 | Top Hat Fixings |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | TOPHAT FIXED TO KARRIER PANEL WITH 2 NO. KSA-FL6 @ 450mm CTRs | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.2 | Helping Hand Bracket |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | HILTI MFT-FOX-HI-100-M-6.5 HELPING HAND BRACKETS FIXED AT 625MM CENTRES | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.3 | Helping Hand Bracket Fixings |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | FIXED TO TOPHAT WITH 1 NO. S-MD-51LS-5.5x50 | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.4 | Helping Had Rails |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | HILTI MFT-L-40x60 HORIZONTAL L RAIL FIXED TO EACH BRACKET WITH INTEGRATED SCREW | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | H | I | R | R
INTERNAL CORNER SEALS
| 6.6 | Aluminium Cladding Panels |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | 2.0mm ALUMINIUM PROFILED SHEET - P.P.C. INTERPON D2525 GOLDEN BEACH | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.7 | Cladding Panel Fixings |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | PANEL FIXED TO HORIZONTAL L RAIL @625mm CTRs WITH SX3-S16-6x29. (8Ø PRE DRILL REQUIRED TO ALUMINIUM SHEET) 1 NO FIXING PER PANEL FIXED POINT NO PRE DRILL REQUIRED FIXED WITH SX5-S16-5.5x31 FOAM FILLER BETWEEN PANEL & RAIL AT TOP & BOTTOM OF PANEL | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
ALUMINIUM CLADDING
| 6.1 | Panels |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | 2.0mm THK ALUMINIUM PLANK P.P.C. MEDIUM BRONZE ULTRA MATT | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
| 6.12 | Panel Fixings |  |  | I |  | 21012-RYD-XX-XX-SP-A-0003_External Walls and Soffit_(A5) Construction_C2 | FIXED DIRECTLY TO KARRIER PANEL WITH KSMR-ALU @400mm CTRs (PRE DRILL REQUIRED) KSSVG25 FOAM TAPE TO BE APPLIED LOCAL TO FIXINGS PENETRATING OUTER SKIN OF PANEL (MIN 50mm LONG) | Check Drawings / Quality Inspection Sheet - Rainscreen Cladding | Daily | Each Zone | Photographs / Joint inspection | Q9 Site Manager | I | I | R | R
Completion Checks | 7.0
7.1
7.2
7.3
7.4
7.5
Testing & Commissioning | 8.0
8.1
8.2
8.3
8.4
8.5
Handover & Close out | 9
9.1
9.2
9.3
9.4
9.5